## Sheet1
Carrier Data
Data Sheet 1
For: | 38YRA018 Outdoor Section of Heat Pump (with CJ5A-018 Indoor Section)
ti = 70oF, 450 cfm inside air
| to (oF) | Heating Capacity* (Mbtu h) | Total PWR** (KW) | ti - inside temperature to - outside temperature
| -3 | 6.33 | 1.33
| 7 | 7.59 | 1.37 | Supplemental heater operates at 242 volts and 30.5 amps.
| 17 | 8.92 | 1.42
| 27 | 10.19 | 1.49
| 37 | 12.13 | 1.57
| 47 | 15.52 | 1.66
| 57 | 17.95 | 1.8
* The Btuh heating capacity values shown are net "integrated" values from which the defrost effect has been subtracted. The Btuh heating from supplement heaters should be added to those values to obtain total system capacity
** The KW value include the compressor, outdoor fan motor, and indoor blower motor. The KW from supplemental heaters should be added to these values to obtain total system kilowatts.