## Sheet1
Data Sheet 3
Time (Θ) Data
Test Date: Feb 08, 2003 Period: 12:45 - 14:18 Eo = 21.4oF
| # | Cycle Mode | Event Description |  | Time (Θ) | Subscripts
E
C -> Capacity
| 1 | Run | 1 | Compressor Start | 0 | CO -> Compressor + fan Off
| 1 | Defrost | 2 | Initiate DF Cycle * | 5.404 | Cy -> Cycle
| 1 | Run | 3 | Terminate DF Cycle | 8.2405 | d -> Defrost
| 1 | Off | 4 | Compressor Stop | 20.1931 | dd -> d-to-d interval
| 2 | Run | 5 | Compressor Start | 30.9218 | i -> inside
| 2 | Defrost | 6 | Initiate DF Cycle | 49.7318 | o -> outside
| 2 | Run | 7 | Terminate DF Cycle | 52.2346 | r -> compressor + fans run
| 2 | Off | 8 | Compressor Stop | 57.2711 | t -> Total System
| 3 | Run | 9 | Compressor Start | 67.1017
| 3 | Off | 10 | Compressor Stop | 88.9367
|  | Run | 11 | Compressor Start | 99.4259 | Clock time = 12:45:37 + Θ(HMS) HMS = hour:min:sec
|  | END | 12 | END of Test | 99.4259
| Cycle | ΔΘr |  | ΔΘCO | ΔΘCy | ΔΘd | ΔΘdd
| 1 | E4 - E1 = 20.1931 |  | E5 - E4 = 10.7287 | E5 - E1 = 30.9218 | E3 - E2 = 2.8365 | E6 - E3 = 30.8842
| 2 | E8 - E5 = 26.3493 |  | E9 - E8 = 9.8306 | E9 - E5 = 36.1799 | E7 - E6 = 2.5628
| 3 | E10 - E9 = 21.8350 |  | E11 - E10 = 10.4892 | E11 - E9 = 32.3242 | 0
| Total | 68.3774 |  | 31.0485 | E11 = 99.4259 | 5.3339 | 30.8842
* 4-way valve reverses refrigerant flow making the defrost mode identical to the cooling mode except that the outer fan motor stops and supplemental ****** resistance heat is turned on to continue warming the conditioned room.