## Sheet1
Example problem: Matching fan to flow requirements
J. M. Cimbala, March 2002 | [8 empty] | for the book:
Fan performance data:
Q (SCFM) | (dP)fan (in. water)
0 | 0.9
250 | 0.95
500 | 0.9
750 | 0.75
1000 | 0.4
1200 | 0
Constants:
Standard SI units
Ru = | 8.3143 | KJ/(kmol K) | = | 8314.3 | J/(kmol K) | universal gas constant
g = | 9.81 | m/s2 | = | 9.81 | m/s2 | gravitational constant
rwater = |  |  | = | 998 | kg/m3 | density of liquid water
Given parameters for the air and the duct:
Air: |  |  |  | Standard SI units
Ru = | 8.3143 | KJ/(kmol K) | = | 8314.3 | J/(kmol K) | universal gas constant
M = | 28.97 | kg/kmol | = | 28.97 | kg/kmol | molecular weight of air
T = | 25 | oC | = | 298.15 | K | air temperature
Pair = | 76 | cm Hg | = | 101300 | N/m2 | atmospheric air pressure
S = |  |  | = | 110.4 | K | Sutherland law temperature, S
T0 = |  |  | = | 273.15 | K | Sutherland law reference temperature, T0
m0 = |  |  | = | 1.71e-05 | kg/(m s) | Sutherland law reference viscosity, m0
m = |  |  | = | 1.8307e-05 | kg/(m s) | viscosity of air (Sutherland law)
r = |  |  | = | 1.1839 | kg/m3 | density of air (ideal gas law)
n = |  |  | = | 1.5464e-05 | m2/s | kinematic viscosity of air
Duct and fittings:
D = | 9.06 | in | = | 0.23012 | m | inner ID of duct
A = | 64.4683 | in2 | = | 0.041592 | m2 | inner cross-sectional area of duct
e = | 0.15 | mm | = | 0.00015 | m | equivalent inner roughness height of duct
e/D = |  |  | = | 0.00065182 |  | roughness factor for inside of duct
L = | 44 | ft | = | 13.4112 | m | length of duct
minor losses | C0 per unit | quantity |  | total C0
hood entry | 1.3 | 1 |  | 1.3 |  | loss coefficient for hood entry
elbow | 0.21 | 5 |  | 1.05 |  | loss coefficient for elbow
other | 0 | 0 |  | 0 |  | loss coefficient for other
other | 0 | 0 |  | 0 |  | loss coefficient for other
SK = |  |  |  | 2.35 |  | total loss coefficient
Calculations: Predict pressure drop through duct for a variety of volume flow rates | [10 empty] | Calculation of Moody chart friction factor |  |  |  |  | Recritical = | 2300
[11 empty] | laminar | turbulent
Q (CFM) | Q (m3/s) | U (m/s) | Re | e/D | f (Moody chart) | VP (N/m2) | DPmajor (N/m2) | DPminor (N/m2) | DPtotal (N/m2) | DPtotal (in. water) | flaminar | fturbulent | final f | denom | fguess | G(f) | G'(f) | new f | G(f) | G'(f) | new f | G(f) | G'(f) | new f | G(f) | G'(f) | new f | G(f) | G'(f) | new f | G(f) | G'(f) | new f | G(f) | G'(f) | new f
50 | 0.023597 | 0.56735 | 8442.79 | 0.00065182 | 0.033227 | 0.19053 | 0.36894 | 0.44775 | 0.81669 | 0.0032842 | 0.0075804 | 0.033227 | 0.033227 | -5.4952 | 0.033116 | 0.010495 | -94.808 | 0.033226 | 2.5254e-05 | -94.3523 | 0.033227 | 1.4684e-10 | -94.3512 | 0.033227 | 0 | -94.3512 | 0.033227 | 0 | -94.3512 | 0.033227 | 0 | -94.3512 | 0.033227 | 0 | -94.3512 | 0.033227
100 | 0.047195 | 1.1347 | 16885.58 | 0.00065182 | 0.028256 | 0.76213 | 1.255 | 1.791 | 3.046 | 0.012249 | 0.0037902 | 0.028256 | 0.028256 | -5.9791 | 0.027972 | 0.03381 | -119.8356 | 0.028254 | 0.00024603 | -118.0987 | 0.028256 | 1.3195e-08 | -118.0861 | 0.028256 | 0 | -118.0861 | 0.028256 | 0 | -118.0861 | 0.028256 | 0 | -118.0861 | 0.028256 | 0 | -118.0861 | 0.028256
200 | 0.094389 | 2.2694 | 33771.16 | 0.00065182 | 0.024612 | 3.0485 | 4.3725 | 7.164 | 11.5365 | 0.046392 | 0.0018951 | 0.024612 | 0.024612 | -6.4167 | 0.024287 | 0.046586 | -145.1559 | 0.024608 | 0.00044673 | -142.387 | 0.024612 | 4.1774e-08 | -142.3603 | 0.024612 | 0 | -142.3603 | 0.024612 | 0 | -142.3603 | 0.024612 | 0 | -142.3603 | 0.024612 | 0 | -142.3603 | 0.024612
300 | 0.14158 | 3.4041 | 50656.7399 | 0.00065182 | 0.022979 | 6.8591 | 9.1856 | 16.119 | 25.3046 | 0.10176 | 0.0012634 | 0.022979 | 0.022979 | -6.6416 | 0.02267 | 0.048593 | -158.9591 | 0.022976 | 0.00047775 | -155.8507 | 0.022979 | 4.6984e-08 | -155.82 | 0.022979 | 0 | -155.82 | 0.022979 | 0 | -155.82 | 0.022979 | 0 | -155.82 | 0.022979 | 0 | -155.82 | 0.022979
400 | 0.18878 | 4.5388 | 67542.3199 | 0.00065182 | 0.022014 | 12.194 | 15.644 | 28.656 | 44.3 | 0.17814 | 0.00094755 | 0.022014 | 0.022014 | -6.7841 | 0.021728 | 0.04758 | -167.8838 | 0.022011 | 0.00045417 | -164.6958 | 0.022014 | 4.2084e-08 | -164.6653 | 0.022014 | 0 | -164.6653 | 0.022014 | 0 | -164.6653 | 0.022014 | 0 | -164.6653 | 0.022014 | 0 | -164.6653 | 0.022014
500 | 0.23597 | 5.6735 | 84427.8999 | 0.00065182 | 0.021365 | 19.0532 | 23.7235 | 44.775 | 68.4984 | 0.27545 | 0.00075804 | 0.021365 | 0.021365 | -6.8841 | 0.021101 | 0.045536 | -174.1806 | 0.021363 | 0.00041406 | -171.029 | 0.021365 | 3.479e-08 | -171.0003 | 0.021365 | 0 | -171.0003 | 0.021365 | 0 | -171.0003 | 0.021365 | 0 | -171.0003 | 0.021365 | 0 | -171.0003 | 0.021365
600 | 0.28317 | 6.8082 | 101313.4799 | 0.00065182 | 0.020895 | 27.4366 | 33.4104 | 64.4759 | 97.8863 | 0.39363 | 0.0006317 | 0.020895 | 0.020895 | -6.9586 | 0.020652 | 0.043167 | -178.8761 | 0.020893 | 0.00037111 | -175.8152 | 0.020895 | 2.7848e-08 | -175.7888 | 0.020895 | 0 | -175.7888 | 0.020895 | 0 | -175.7888 | 0.020895 | 0 | -175.7888 | 0.020895 | 0 | -175.7888 | 0.020895
700 | 0.33036 | 7.9429 | 118199.0598 | 0.00065182 | 0.020537 | 37.3442 | 44.6961 | 87.7589 | 132.4551 | 0.53264 | 0.00054146 | 0.020537 | 0.020537 | -7.0165 | 0.020312 | 0.04076 | -182.5164 | 0.020535 | 0.00033035 | -179.5713 | 0.020537 | 2.2012e-08 | -179.5474 | 0.020537 | 0 | -179.5474 | 0.020537 | 0 | -179.5474 | 0.020537 | 0 | -179.5474 | 0.020537 | 0 | -179.5474 | 0.020537
800 | 0.37756 | 9.0776 | 135084.6398 | 0.00065182 | 0.020255 | 48.7761 | 57.5752 | 114.6239 | 172.1991 | 0.69246 | 0.00047378 | 0.020255 | 0.020255 | -7.063 | 0.020046 | 0.038436 | -185.4225 | 0.020253 | 0.00029346 | -182.6031 | 0.020255 | 1.734e-08 | -182.5816 | 0.020255 | 0 | -182.5816 | 0.020255 | 0 | -182.5816 | 0.020255 | 0 | -182.5816 | 0.020255 | 0 | -182.5816 | 0.020255
900 | 0.42475 | 10.2123 | 151970.2198 | 0.00065182 | 0.020025 | 61.7323 | 72.0436 | 145.0709 | 217.1145 | 0.87308 | 0.00042114 | 0.020025 | 0.020025 | -7.1012 | 0.019831 | 0.036243 | -187.7963 | 0.020024 | 0.00026078 | -185.1046 | 0.020025 | 1.3675e-08 | -185.0851 | 0.020025 | 0 | -185.0851 | 0.020025 | 0 | -185.0851 | 0.020025 | 0 | -185.0851 | 0.020025 | 0 | -185.0851 | 0.020025
1000 | 0.47195 | 11.347 | 168855.7998 | 0.00065182 | 0.019835 | 76.2127 | 88.0987 | 179.0998 | 267.1985 | 1.0745 | 0.00037902 | 0.019835 | 0.019835 | -7.1331 | 0.019654 | 0.034198 | -189.7715 | 0.019834 | 0.00023211 | -187.2051 | 0.019835 | 1.0822e-08 | -187.1877 | 0.019835 | 0 | -187.1877 | 0.019835 | 0 | -187.1877 | 0.019835 | 0 | -187.1877 | 0.019835 | 0 | -187.1877 | 0.019835
1100 | 0.51914 | 12.4817 | 185741.3797 | 0.00065182 | 0.019675 | 92.2174 | 105.7382 | 216.7108 | 322.449 | 1.2967 | 0.00034457 | 0.019675 | 0.019675 | -7.1602 | 0.019505 | 0.0323 | -191.4404 | 0.019674 | 0.00020704 | -188.9949 | 0.019675 | 8.604e-09 | -188.9792 | 0.019675 | 0 | -188.9792 | 0.019675 | 0 | -188.9792 | 0.019675 | 0 | -188.9792 | 0.019675 | 0 | -188.9792 | 0.019675
1200 | 0.56634 | 13.6164 | 202626.9597 | 0.00065182 | 0.019538 | 109.7463 | 124.9607 | 257.9037 | 382.8645 | 1.5396 | 0.00031585 | 0.019538 | 0.019538 | -7.1836 | 0.019379 | 0.030544 | -192.869 | 0.019537 | 0.00018514 | -190.5387 | 0.019538 | 6.8754e-09 | -190.5246 | 0.019538 | 0 | -190.5246 | 0.019538 | 0 | -190.5246 | 0.019538 | 0 | -190.5246 | 0.019538 | 0 | -190.5246 | 0.019538