## Sheet1
Reach of a Flanged Line Sink in a Streaming Flow
J. M. Cimbala, July 2001
Constants:
Q/L = | 30 | m2/min
U0 = | 30.5 | m/min
Calculations:
r0 = | 0.31309 | m
hinfinity = | 0.98361 | m
h0 = | 0.4918 | m
|  | yd = | 30 | m2/min | Velocity components along dividing streamline: | [5 empty] | r vs q: for Umin = | 200 | FPM | = | 60.96 | m/min |  | r vs q: for Umin = | 150 | FPM | = | 45.72 | m/min |  | r vs q: for Umin = | 120 | FPM | = | 36.576 | m/min
q (degrees) | q (radians) | r (m) | x (m) | y (m) | Ur (m/s) | Uq (m/s) | Ux (m/s) | Uy (m/s) | Ua (m/s) | a | b | c | r (+) | r (-) | x (m) | y (m) | a | b | c | r (+) | r (-) | x (m) | y (m) | a | b | c | r (+) | r (-) | x (m) | y (m)
1 | 0.017453 | 56.0463 | 56.0377 | 0.97814 | -0.5111 | 0.0088716 | -0.51117 | -4.956e-05 | 0.51117 | 2785.8716 | -582.4184 | -91.1891 | 0.31348 | -0.10442 | 0.31343 | 0.005471 | 1160.0684 | -582.4184 | -91.1891 | 0.62735 | -0.1253 | 0.62726 | 0.010949 | 407.5538 | -582.4184 | -91.1891 | 1.5714 | -0.14238 | 1.5712 | 0.027425
2 | 0.034907 | 27.8708 | 27.8538 | 0.97268 | -0.51373 | 0.017741 | -0.51404 | -0.00019929 | 0.51404 | 2785.8716 | -582.1522 | -91.1891 | 0.31341 | -0.10444 | 0.31322 | 0.010938 | 1160.0684 | -582.1522 | -91.1891 | 0.62716 | -0.12534 | 0.62678 | 0.021888 | 407.5538 | -582.1522 | -91.1891 | 1.5708 | -0.14244 | 1.5699 | 0.054822
3 | 0.05236 | 18.4809 | 18.4555 | 0.96721 | -0.51625 | 0.026604 | -0.51693 | -0.00045071 | 0.51693 | 2785.8716 | -581.7088 | -91.1891 | 0.31329 | -0.10448 | 0.31286 | 0.016396 | 1160.0684 | -581.7088 | -91.1891 | 0.62684 | -0.1254 | 0.62599 | 0.032806 | 407.5538 | -581.7088 | -91.1891 | 1.5698 | -0.14253 | 1.5677 | 0.082159
4 | 0.069813 | 13.7872 | 13.7536 | 0.96175 | -0.51864 | 0.03546 | -0.51985 | -0.00080524 | 0.51985 | 2785.8716 | -581.0881 | -91.1891 | 0.31312 | -0.10454 | 0.31236 | 0.021842 | 1160.0684 | -581.0881 | -91.1891 | 0.6264 | -0.12549 | 0.62487 | 0.043695 | 407.5538 | -581.0881 | -91.1891 | 1.5685 | -0.14266 | 1.5646 | 0.10941
5 | 0.087266 | 10.9721 | 10.9304 | 0.95628 | -0.5209 | 0.044304 | -0.52278 | -0.0012642 | 0.52279 | 2785.8716 | -580.2905 | -91.1891 | 0.31291 | -0.10461 | 0.31172 | 0.027272 | 1160.0684 | -580.2905 | -91.1891 | 0.62583 | -0.1256 | 0.62344 | 0.054544 | 407.5538 | -580.2905 | -91.1891 | 1.5667 | -0.14282 | 1.5607 | 0.13654
6 | 0.10472 | 9.0963 | 9.0464 | 0.95082 | -0.52305 | 0.053135 | -0.52573 | -0.0018289 | 0.52574 | 2785.8716 | -579.3161 | -91.1891 | 0.31264 | -0.1047 | 0.31093 | 0.03268 | 1160.0684 | -579.3161 | -91.1891 | 0.62513 | -0.12575 | 0.6217 | 0.065343 | 407.5538 | -579.3161 | -91.1891 | 1.5645 | -0.14302 | 1.5559 | 0.16353
7 | 0.12217 | 7.7571 | 7.6993 | 0.94536 | -0.52506 | 0.06195 | -0.5287 | -0.0025004 | 0.5287 | 2785.8716 | -578.1652 | -91.1891 | 0.31233 | -0.1048 | 0.31001 | 0.038064 | 1160.0684 | -578.1652 | -91.1891 | 0.6243 | -0.12591 | 0.61965 | 0.076083 | 407.5538 | -578.1652 | -91.1891 | 1.5619 | -0.14326 | 1.5502 | 0.19035
8 | 0.13963 | 6.7534 | 6.6877 | 0.93989 | -0.52695 | 0.070746 | -0.53167 | -0.0032798 | 0.53168 | 2785.8716 | -576.8382 | -91.1891 | 0.31198 | -0.10492 | 0.30894 | 0.043419 | 1160.0684 | -576.8382 | -91.1891 | 0.62335 | -0.1261 | 0.61728 | 0.086753 | 407.5538 | -576.8382 | -91.1891 | 1.5589 | -0.14353 | 1.5437 | 0.21696
9 | 0.15708 | 5.9733 | 5.8997 | 0.93443 | -0.52872 | 0.079521 | -0.53465 | -0.0041681 | 0.53467 | 2785.8716 | -575.3355 | -91.1891 | 0.31157 | -0.10506 | 0.30774 | 0.048741 | 1160.0684 | -575.3355 | -91.1891 | 0.62227 | -0.12632 | 0.61461 | 0.097345 | 407.5538 | -575.3355 | -91.1891 | 1.5555 | -0.14384 | 1.5364 | 0.24334
10 | 0.17453 | 5.3497 | 5.2684 | 0.92896 | -0.53036 | 0.088271 | -0.53763 | -0.0051661 | 0.53766 | 2785.8716 | -573.6575 | -91.1891 | 0.31112 | -0.10521 | 0.3064 | 0.054026 | 1160.0684 | -573.6575 | -91.1891 | 0.62107 | -0.12657 | 0.61163 | 0.10785 | 407.5538 | -573.6575 | -91.1891 | 1.5518 | -0.14419 | 1.5282 | 0.26946
15 | 0.2618 | 3.4837 | 3.365 | 0.90164 | -0.5367 | 0.13157 | -0.55246 | -0.011824 | 0.55259 | 2785.8716 | -562.6586 | -91.1891 | 0.30818 | -0.10621 | 0.29768 | 0.079763 | 1160.0684 | -562.6586 | -91.1891 | 0.61321 | -0.12819 | 0.59232 | 0.15871 | 407.5538 | -562.6586 | -91.1891 | 1.5271 | -0.14652 | 1.4751 | 0.39524
20 | 0.34907 | 2.5563 | 2.4022 | 0.87432 | -0.53994 | 0.17386 | -0.56684 | -0.021294 | 0.56724 | 2785.8716 | -547.3776 | -91.1891 | 0.30412 | -0.10763 | 0.28578 | 0.10401 | 1160.0684 | -547.3776 | -91.1891 | 0.60235 | -0.1305 | 0.56602 | 0.20602 | 407.5538 | -547.3776 | -91.1891 | 1.4929 | -0.14987 | 1.4029 | 0.51062
25 | 0.43633 | 2.0042 | 1.8164 | 0.84699 | -0.54012 | 0.21483 | -0.58031 | -0.033561 | 0.58127 | 2785.8716 | -527.9307 | -91.1891 | 0.29898 | -0.10948 | 0.27097 | 0.12636 | 1160.0684 | -527.9307 | -91.1891 | 0.58863 | -0.13354 | 0.53348 | 0.24876 | 407.5538 | -527.9307 | -91.1891 | 1.4497 | -0.15434 | 1.3139 | 0.61267
30 | 0.5236 | 1.6393 | 1.4197 | 0.81967 | -0.53731 | 0.25417 | -0.59241 | -0.048542 | 0.5944 | 2785.8716 | -504.4659 | -91.1891 | 0.29285 | -0.11177 | 0.25362 | 0.14643 | 1160.0684 | -504.4659 | -91.1891 | 0.57223 | -0.13737 | 0.49556 | 0.28611 | 407.5538 | -504.4659 | -91.1891 | 1.3979 | -0.16006 | 1.2106 | 0.69893
35 | 0.61087 | 1.3814 | 1.1316 | 0.79235 | -0.53161 | 0.29157 | -0.60271 | -0.066082 | 0.60632 | 2785.8716 | -477.1619 | -91.1891 | 0.28581 | -0.11453 | 0.23412 | 0.16393 | 1160.0684 | -477.1619 | -91.1891 | 0.55337 | -0.14205 | 0.4533 | 0.3174 | 407.5538 | -477.1619 | -91.1891 | 1.338 | -0.16722 | 1.096 | 0.76746
40 | 0.69813 | 1.1902 | 0.91172 | 0.76503 | -0.52313 | 0.32675 | -0.61077 | -0.085956 | 0.61679 | 2785.8716 | -446.2263 | -91.1891 | 0.27794 | -0.11777 | 0.21292 | 0.17866 | 1160.0684 | -446.2263 | -91.1891 | 0.53232 | -0.14767 | 0.40778 | 0.34217 | 407.5538 | -446.2263 | -91.1891 | 1.2709 | -0.17605 | 0.9736 | 0.81694
45 | 0.7854 | 1.0433 | 0.7377 | 0.7377 | -0.512 | 0.35945 | -0.61621 | -0.10787 | 0.62558 | 2785.8716 | -411.8947 | -91.1891 | 0.26937 | -0.12152 | 0.19047 | 0.19047 | 1160.0684 | -411.8947 | -91.1891 | 0.50938 | -0.15432 | 0.36019 | 0.36019 | 407.5538 | -411.8947 | -91.1891 | 1.1975 | -0.18685 | 0.84676 | 0.84676
50 | 0.87266 | 0.92734 | 0.59608 | 0.71038 | -0.49838 | 0.38941 | -0.61865 | -0.13147 | 0.63247 | 2785.8716 | -374.4283 | -91.1891 | 0.2602 | -0.1258 | 0.16725 | 0.19933 | 1160.0684 | -374.4283 | -91.1891 | 0.48488 | -0.16212 | 0.31167 | 0.37144 | 407.5538 | -374.4283 | -91.1891 | 1.1187 | -0.2 | 0.7191 | 0.85699
55 | 0.95993 | 0.83386 | 0.47828 | 0.68306 | -0.48243 | 0.4164 | -0.61781 | -0.15635 | 0.63729 | 2785.8716 | -334.1123 | -91.1891 | 0.25057 | -0.13063 | 0.14372 | 0.20525 | 1160.0684 | -334.1123 | -91.1891 | 0.45919 | -0.17118 | 0.26338 | 0.37615 | 407.5538 | -334.1123 | -91.1891 | 1.0358 | -0.21601 | 0.59412 | 0.84849
60 | 1.0472 | 0.75718 | 0.37859 | 0.65574 | -0.46436 | 0.44023 | -0.61343 | -0.18203 | 0.63987 | 2785.8716 | -291.2535 | -91.1891 | 0.2406 | -0.13605 | 0.1203 | 0.20836 | 1160.0684 | -291.2535 | -91.1891 | 0.43272 | -0.18166 | 0.21636 | 0.37475 | 407.5538 | -291.2535 | -91.1891 | 0.95013 | -0.23549 | 0.47506 | 0.82284
65 | 1.1345 | 0.69338 | 0.29303 | 0.62842 | -0.44437 | 0.46071 | -0.60534 | -0.20803 | 0.64009 | 2785.8716 | -246.1781 | -91.1891 | 0.23042 | -0.14206 | 0.097381 | 0.20883 | 1160.0684 | -246.1781 | -91.1891 | 0.40588 | -0.19367 | 0.17153 | 0.36785 | 407.5538 | -246.1781 | -91.1891 | 0.86323 | -0.2592 | 0.36482 | 0.78236
70 | 1.2217 | 0.63967 | 0.21878 | 0.60109 | -0.42267 | 0.47768 | -0.59343 | -0.2338 | 0.63783 | 2785.8716 | -199.2292 | -91.1891 | 0.22018 | -0.14866 | 0.075305 | 0.2069 | 1160.0684 | -199.2292 | -91.1891 | 0.37909 | -0.20735 | 0.12966 | 0.35623 | 407.5538 | -199.2292 | -91.1891 | 0.77686 | -0.28802 | 0.2657 | 0.73001
75 | 1.309 | 0.59401 | 0.15374 | 0.57377 | -0.3995 | 0.49101 | -0.57768 | -0.2588 | 0.633 | 2785.8716 | -150.7639 | -91.1891 | 0.20999 | -0.15588 | 0.05435 | 0.20284 | 1160.0684 | -150.7639 | -91.1891 | 0.35278 | -0.22282 | 0.091306 | 0.34076 | 407.5538 | -150.7639 | -91.1891 | 0.69286 | -0.32293 | 0.17932 | 0.66925
80 | 1.3963 | 0.55488 | 0.096354 | 0.54645 | -0.3751 | 0.50061 | -0.55814 | -0.28247 | 0.62555 | 2785.8716 | -101.1513 | -91.1891 | 0.19998 | -0.16368 | 0.034727 | 0.19695 | 1160.0684 | -101.1513 | -91.1891 | 0.32734 | -0.24014 | 0.056841 | 0.32236 | 407.5538 | -101.1513 | -91.1891 | 0.61312 | -0.36493 | 0.10647 | 0.60381
85 | 1.4835 | 0.52111 | 0.045418 | 0.51913 | -0.34972 | 0.5064 | -0.53495 | -0.30425 | 0.61542 | 2785.8716 | -50.7688 | -91.1891 | 0.19026 | -0.17204 | 0.016583 | 0.18954 | 1160.0684 | -50.7688 | -91.1891 | 0.3031 | -0.25934 | 0.026417 | 0.30195 | 407.5538 | -50.7688 | -91.1891 | 0.53939 | -0.41482 | 0.047011 | 0.53733
90 | 1.5708 | 0.4918 | 3.0127e-17 | 0.4918 | -0.32362 | 0.50833 | -0.50833 | -0.32362 | 0.6026 | 2785.8716 | -3.5683e-14 | -91.1891 | 0.18092 | -0.18092 | 1.1083e-17 | 0.18092 | 1160.0684 | -3.5683e-14 | -91.1891 | 0.28037 | -0.28037 | 1.7175e-17 | 0.28037 | 407.5538 | -3.5683e-14 | -91.1891 | 0.47302 | -0.47302 | 2.8976e-17 | 0.47302
95 | 1.6581 | 0.46626 | -0.040637 | 0.46448 | -0.29704 | 0.5064 | -0.47858 | -0.34005 | 0.58709 | 2785.8716 | 50.7688 | -91.1891 | 0.17204 | -0.19026 | -0.014994 | 0.17138 | 1160.0684 | 50.7688 | -91.1891 | 0.25934 | -0.3031 | -0.022603 | 0.25835 | 407.5538 | 50.7688 | -91.1891 | 0.41482 | -0.53939 | -0.036154 | 0.41324
100 | 1.7453 | 0.4439 | -0.077083 | 0.43716 | -0.27026 | 0.50061 | -0.44607 | -0.35309 | 0.56891 | 2785.8716 | 101.1513 | -91.1891 | 0.16368 | -0.19998 | -0.028422 | 0.16119 | 1160.0684 | 101.1513 | -91.1891 | 0.24014 | -0.32734 | -0.0417 | 0.23649 | 407.5538 | 101.1513 | -91.1891 | 0.36493 | -0.61312 | -0.06337 | 0.35939
105 | 1.8326 | 0.42429 | -0.10982 | 0.40984 | -0.24354 | 0.49101 | -0.41125 | -0.36232 | 0.54809 | 2785.8716 | 150.7639 | -91.1891 | 0.15588 | -0.20999 | -0.040344 | 0.15056 | 1160.0684 | 150.7639 | -91.1891 | 0.22282 | -0.35278 | -0.05767 | 0.21523 | 407.5538 | 150.7639 | -91.1891 | 0.32293 | -0.69286 | -0.083581 | 0.31193
110 | 1.9199 | 0.40706 | -0.13922 | 0.38251 | -0.21712 | 0.47768 | -0.37461 | -0.3674 | 0.52471 | 2785.8716 | 199.2292 | -91.1891 | 0.14866 | -0.22018 | -0.050846 | 0.1397 | 1160.0684 | 199.2292 | -91.1891 | 0.20735 | -0.37909 | -0.070919 | 0.19485 | 407.5538 | 199.2292 | -91.1891 | 0.28802 | -0.77686 | -0.098507 | 0.27065
115 | 2.0071 | 0.39191 | -0.16563 | 0.35519 | -0.19127 | 0.46071 | -0.33671 | -0.36805 | 0.49883 | 2785.8716 | 246.1781 | -91.1891 | 0.14206 | -0.23042 | -0.060035 | 0.12875 | 1160.0684 | 246.1781 | -91.1891 | 0.19367 | -0.40588 | -0.081848 | 0.17552 | 407.5538 | 246.1781 | -91.1891 | 0.2592 | -0.86323 | -0.10954 | 0.23491
120 | 2.0944 | 0.37859 | -0.1893 | 0.32787 | -0.16622 | 0.44023 | -0.29814 | -0.36407 | 0.47057 | 2785.8716 | 291.2535 | -91.1891 | 0.13605 | -0.2406 | -0.068024 | 0.11782 | 1160.0684 | 291.2535 | -91.1891 | 0.18166 | -0.43272 | -0.090828 | 0.15732 | 407.5538 | 291.2535 | -91.1891 | 0.23549 | -0.95013 | -0.11775 | 0.20394
125 | 2.1817 | 0.3669 | -0.21044 | 0.30055 | -0.14222 | 0.4164 | -0.25953 | -0.35533 | 0.44002 | 2785.8716 | 334.1123 | -91.1891 | 0.13063 | -0.25057 | -0.074929 | 0.10701 | 1160.0684 | 334.1123 | -91.1891 | 0.17118 | -0.45919 | -0.098187 | 0.14023 | 407.5538 | 334.1123 | -91.1891 | 0.21601 | -1.0358 | -0.1239 | 0.17695
130 | 2.2689 | 0.35667 | -0.22926 | 0.27322 | -0.11948 | 0.38941 | -0.2215 | -0.34183 | 0.40732 | 2785.8716 | 374.4283 | -91.1891 | 0.1258 | -0.2602 | -0.080861 | 0.096367 | 1160.0684 | 374.4283 | -91.1891 | 0.16212 | -0.48488 | -0.10421 | 0.12419 | 407.5538 | 374.4283 | -91.1891 | 0.2 | -1.1187 | -0.12856 | 0.15321
135 | 2.3562 | 0.34776 | -0.2459 | 0.2459 | -0.098215 | 0.35945 | -0.18472 | -0.32362 | 0.37262 | 2785.8716 | 411.8947 | -91.1891 | 0.12152 | -0.26937 | -0.085925 | 0.085925 | 1160.0684 | 411.8947 | -91.1891 | 0.15432 | -0.50938 | -0.10912 | 0.10912 | 407.5538 | 411.8947 | -91.1891 | 0.18685 | -1.1975 | -0.13212 | 0.13212
140 | 2.4435 | 0.34005 | -0.26049 | 0.21858 | -0.07863 | 0.32675 | -0.1498 | -0.30085 | 0.33608 | 2785.8716 | 446.2263 | -91.1891 | 0.11777 | -0.27794 | -0.090215 | 0.0757 | 1160.0684 | 446.2263 | -91.1891 | 0.14767 | -0.53232 | -0.11312 | 0.094919 | 407.5538 | 446.2263 | -91.1891 | 0.17605 | -1.2709 | -0.13486 | 0.11316
145 | 2.5307 | 0.33345 | -0.27314 | 0.19126 | -0.060901 | 0.29157 | -0.11735 | -0.27377 | 0.29786 | 2785.8716 | 477.1619 | -91.1891 | 0.11453 | -0.28581 | -0.093815 | 0.06569 | 1160.0684 | 477.1619 | -91.1891 | 0.14205 | -0.55337 | -0.11636 | 0.081477 | 407.5538 | 477.1619 | -91.1891 | 0.16722 | -1.338 | -0.13698 | 0.095915
150 | 2.618 | 0.32787 | -0.28394 | 0.16393 | -0.045193 | 0.25417 | -0.087945 | -0.24271 | 0.25815 | 2785.8716 | 504.4659 | -91.1891 | 0.11177 | -0.29285 | -0.096797 | 0.055886 | 1160.0684 | 504.4659 | -91.1891 | 0.13737 | -0.57223 | -0.11897 | 0.068685 | 407.5538 | 504.4659 | -91.1891 | 0.16006 | -1.3979 | -0.13862 | 0.080032
155 | 2.7053 | 0.32325 | -0.29297 | 0.13661 | -0.03165 | 0.21483 | -0.062107 | -0.20808 | 0.21715 | 2785.8716 | 527.9307 | -91.1891 | 0.10948 | -0.29898 | -0.099223 | 0.046268 | 1160.0684 | 527.9307 | -91.1891 | 0.13354 | -0.58863 | -0.12103 | 0.056437 | 407.5538 | 527.9307 | -91.1891 | 0.15434 | -1.4497 | -0.13988 | 0.065227
160 | 2.7925 | 0.31954 | -0.30027 | 0.10929 | -0.020396 | 0.17386 | -0.040298 | -0.17035 | 0.17505 | 2785.8716 | 547.3776 | -91.1891 | 0.10763 | -0.30412 | -0.10114 | 0.036812 | 1160.0684 | 547.3776 | -91.1891 | 0.1305 | -0.60235 | -0.12263 | 0.044634 | 407.5538 | 547.3776 | -91.1891 | 0.14987 | -1.4929 | -0.14083 | 0.051258
165 | 2.8798 | 0.3167 | -0.30591 | 0.081967 | -0.011534 | 0.13157 | -0.022911 | -0.13007 | 0.13207 | 2785.8716 | 562.6586 | -91.1891 | 0.10621 | -0.30818 | -0.10259 | 0.02749 | 1160.0684 | 562.6586 | -91.1891 | 0.12819 | -0.61321 | -0.12382 | 0.033178 | 407.5538 | 562.6586 | -91.1891 | 0.14652 | -1.5271 | -0.14153 | 0.037922
170 | 2.9671 | 0.31469 | -0.30991 | 0.054645 | -0.0051459 | 0.088271 | -0.01026 | -0.087824 | 0.088421 | 2785.8716 | 573.6575 | -91.1891 | 0.10521 | -0.31112 | -0.10361 | 0.018269 | 1160.0684 | 573.6575 | -91.1891 | 0.12657 | -0.62107 | -0.12464 | 0.021978 | 407.5538 | 573.6575 | -91.1891 | 0.14419 | -1.5518 | -0.142 | 0.025038
175 | 3.0543 | 0.31349 | -0.3123 | 0.027322 | -0.0012894 | 0.044304 | -0.0025769 | -0.044248 | 0.044323 | 2785.8716 | 580.2905 | -91.1891 | 0.10461 | -0.31291 | -0.10421 | 0.0091172 | 1160.0684 | 580.2905 | -91.1891 | 0.1256 | -0.62583 | -0.12513 | 0.010947 | 407.5538 | 580.2905 | -91.1891 | 0.14282 | -1.5667 | -0.14227 | 0.012447
179.9999 | 3.1416 | 0.31309 | -0.31309 | 5.4645e-07 | -6.8153e-11 | 8.8721e-07 | 6.6604e-11 | -8.8721e-07 | 8.8721e-07 | 2785.8716 | 582.5071 | -91.1891 | 0.10441 | -0.3135 | -0.10441 | 1.8223e-07 | 1160.0684 | 582.5071 | -91.1891 | 0.12529 | -0.62742 | -0.12529 | 2.1867e-07 | 407.5538 | 582.5071 | -91.1891 | 0.14237 | -1.5716 | -0.14237 | 2.4847e-07